Energy Management system With Deep Reinforcement Learning

Date: 07/10/2026

Total Energy requirement of battery

Total Load Energy

| System Component | Qty | Voltage | Current (A) | Power P = IV (Watts) | Duration (hr) | Energy/day (Wh) |
| --- | --- | --- | --- | --- | --- | --- |
| 5V bulb | 2 | 5V | 1 | 10W with a buck converter which has efficiency of 80% yields about 12.5W | 5 | 62.5 |
| Dc Fan | 1 | 12V | 0.83 | 10 | 6 | 60 |
| Phone (via USB buck 3 × 12W out) | 3 | 5V | 2.4 | 36W with an efficiency of 88% yields about 41W | 1.5 | 61.5 |
| Load Total |  |  |  | 63.5 W |  | 184 Wh |
| Micro controller power/Energy Budget For the purpose of having enough margin, I want to use this power profile for the ESP32 to make up for my inability to enter too many details about what connects to it: ESP32 (its Wi-fi and Bluetooth active at 0.25A) + 5 sensors (5v 0.07A) + 3 relays (5v 0.07A) + 5 LED (5v 0.02A) The sensors would stay on for 24 hours, Let’s assume that at least 3 LED would be on for 12 hours, this assumption would make up for the power used by those LEDs that come on for few seconds and go off, Let assume that the 5 NC relays are for controlling 5 states and they would be energized for 4 hours before the BMS cuts of power discharge from the battery The ESP32 will connect via an LM2596 buck converter which has a maximum current rating of 3.0 Amps but a safe current output of 1.5A. So, the total current loads connecting to this buck converter should not exceed 1.5A |  |  |  |  |  |  |
| ESP32 (Wi-Fi & Bluetooth active) – always on, via a buck converter | 1 | 3v – 5v | 0.25 | 1.25W | 24 | 30Wh |
| 5 sensors | 5 | 5v | 0.07A | 1.75 | 24 | 42 |
| 3 LEDs (5V × 0.02 A = 0.1 W each) | 3 | 5v | 0.02 | 0.3 | 12 | 3.6 |
| 5 relays (0.35 W each) | 5 | 5v | 0.07A | 1.75 | 4 | 7Wh |
| Micro-controller Load Total |  |  |  | 5.05 W Peak |  | 82.6 Wh |
| Factoring in Buck converter efficiency of 80% Basic LM2596 modules are typically 75-85% efficient at these loads, and 80% is a reasonable conservative figure. | 5.05W with an efficiency of 80% yields about 6.3W Applying same efficiency to the total micro controller load energy yield 103Wh |  |  |  |  |  |
| Load Total |  |  |  | 63.5 + 6.3 = 69.8W |  | 184 + 103 = 287Wh |
| Peak load: about 69.8 W, or 5.8 A at 12V. This is when everything runs at once. Base load: (1.25 + 1.75 + 0.30 = 3.3) W. This is the controller and the load drawing power at the state of rest. I included the LED because one or two LEDs stay on for a good number of times. Average load: daily 287h ÷ 24, about 12 W. Daily energy: about 287 Wh. |  |  |  |  |  |  |

2. Wire Sizing

The Wire sizing should be done before factoring other loses because wire loss occurs on the load side, so it must go in before you factor DOD, BMS, converter losses. Correct order: (287 + wire)

| Current drawn through wire | Highest load voltage | Length of Wire (Round trip) | Corresponding gauge of wire | Resistance of wire | Voltage Loss by wire | Power Loss by wire | Energy Loss by wire | Fuse current |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 5.8A | 12V | 900cm (18m) | Based on AWG chart, corresponding guage is 10AWG | R = rho x L/A = 0.0589 Ω | V_drop = I x R V_drop = 0.34162 | P = I²R | E = I²R × hr One load runs for 6 hours, so I will use that as the run time | Max current wire can carry + 25% of the max current = 7.25A |

Resistance of wire

R = rho x L/A

where:

- R is resistance.

- rho is the conductor material's resistivity for copper it is 1.72 x 10^-2 ohms per meter

- L is the conductor length (on both the positive and negative)

- A is the cross-sectional area (to calculate this, use a wire gauge to get the diameter, and use this formula “A=π(d/2)^2 where d is the conductor diameter.” to get the cross-sectional area from the diameter)

However, every AWG have standard cross sectional area value, for 10AWG, it cross-sectional area value is 5.26 mm²

R = rho x L/A

R = 1.72 x 10^-2  x 18/(5.26 x 10^-6)m^2

R = 0.0589 Ω

Voltage drop of wire

V_drop = I x R

V_drop = 5.8 x 0.0589

V_drop = 0.34162

Power Loss by wire

P = I²R

P = 5.8² x 0.0589

P = 1.98W

Energy Loss by wire

E = I²R × hours.

One load runs for 6 hours, so I will use that as the run time

E = I²R × hours.

E = I²R x 6

E = 5.8² x 0.0589 x 6

E = 11.8886Wh

Chosen fuse

Max current wire can carry + 25% of the max current

5.8A + (5.8 x25/100)

= 7.25A round is up to 10A (which is a standard fuse).

It is below the wire’s ampacity. 10AWG carries about 30 A or more, so a 10 A fuse is easily protected.

Note: Always place the fuse holder as close to the 12V power source (battery) as possible—ideally within 7 inches (18 cm) of the positive terminal. If a short circuit occurs halfway down your 18-meter wire run, a fuse placed at the far end near the device will do nothing to stop the main wire from melting.

Current Energy level: 287 + 11.9 = 298.9Wh

3. Energy loses

Cable loss, Fuse loss, BMS loss, converter loss, Depth of discharge loss, Engineering loss

| Factoring in Losses |  |  |  |  |
| --- | --- | --- | --- | --- |
| BMS efficiency is 97% (meaning 3% energy loss) | E = output power /input 97% = 298.9/in Input = 298.9/0.97 = 308.14Wh |  | 308.14Wh |  |
| Adding a Depth of Discharge of 75% (for Li-ion battery) it changes to 50% for Lead -acid | 308.14/0.75 |  | 410.9Wh |  |
| 20 % Engineering Energy Loss due to aging, and unplanned use | (20/100 x 410.9) = 82.18Wh |  | 82.18Wh |  |

4. Battery Capacity Requirement

| Here are the loses considered Cable loss, Fuse loss, BMS loss, converter loss, Depth of discharge loss, Engineering loss E_battery = E_load +E_wire losses +E_other losses |  |  |
| --- | --- | --- |
| Battery Energy | Load energy with all eff + Eng. Loss = 410.9 + 82.18 | 493Wh |
| Battery Capacity = IVh / V 493/11.1V (using nominal voltage) = 44.4Ah |  |  |

🔋5. Lithium-ion Battery Sizing & Configuration

To determine the battery configuration, since I already know my overall battery capacity (44.4Ah), building with a Li-ion 3.7v 1.5Ah

To get the number of Parallel cells

To get the number of parallels in the configuration, I will divide the overall battery capacity by the single cell capacity, that gives 44.4/1.5 = 29.6, Approx. 30 cells in parallel

To get the number of series cells

To get the number of series in the configuration, I will divide the pack voltage by the single cell voltage, that gives 11.1/3.7 = 3 cells in series.

Total number of cells

No. of parallel cell x no of series cells

30 x 3 = 90 cells

Pack Energy 45Ah x 11.1 = 500Wh

🔋 6. Solar panel sizing and configuration

The solar panel needs to power the load and charge the battery during the daytime.

Total Combined System Load:
Because your night load is equal to your day load, we combine them at the very beginning before working backwards through the system losses.

Daytime Load = 287 Wh

Nighttime Load

At night we turn the DC fan 60Wh off, we turn one 5v bulb 31.25Wh off, turn off all phone charging 61.5Wh

= 287 – 60 - 31.25 - 61.5 = 134.25

Base Combined Load = 287 + 134.25 = 421.25 Wh

Working Backwards Through the System Losses:
Panel → panel cable → Schottky diode → Charge controller (Buck converter CC/CV) → Combined Load

- Combined Load + Wire Energy loss
421.25 Wh + 11.9 Wh = 433.15 Wh

The solar system therefore needs to provide approximately 433.15 Wh before accounting for the other losses.

- Factoring in 18% solar Energy loss (Heat, dust, and panel mismatch)
433.15 + (0.18 x 433.15) = 528.23 Wh

- Factoring in 96% charge controller efficiency (XL4016 CC/CV buck converter)
Input = 528.23 / 0.96 = 550.24Wh

- Factoring in panel battery charging and general system loss (20%)
To make up for round-trip charging inefficiencies and resistance, we add 20%:
550.24 + (0.20 x 550.24) = 660.3 Wh

Required Panel Wattage:

- Total Panel Wh needed = 660.3 Wh

- Peak sun hour 4.5hr

- Required Panel Wattage = 660.3 Wh / 4.5 hours = 147 Watts

7. Charge Controller Sizing

Determining solar panel capacity

First, we convert your energy (88.8Wh) into Amp-hours (Ah) to see how much "room" is in the tank.

- Total Energy: 485.3Wh

- Nominal Voltage (4S): 11.1V

- Capacity: 485.3Wh / 11.1V = 43.7Ah

2. Choosing the Amperage

For Lithium-ion, the standard charging rate is usually between 0.2C (gentle) and 0.5C (fast).

- The "Gentle" Rate (0.2C): 43.7Ah x 0.2 = 8.74A

  - Best for: Maximizing the lifespan of your cells. The battery will stay cool.

- The "Standard" Rate (0.3C): 43.7Ah x 0.3 = 13.11A

  - Best for: A great balance between speed and battery health.

- The "Fast" Rate (0.5C): 43.7Ah 0.5 = 21.85A

Choosing the Charging Rate (C-Rating)

For Lithium-ion health, I aim for a balance between speed and cell longevity.

- The "Safe" Rate (0.25C): 43.7Ah x 0.25 = 11A.

- Why this is perfect: The 110W Solar Panel at 19V naturally outputs approximately 5.8A 110W/ 19V.

5.8A does not match my gentle 1.9A–2.25A target. In fact, 5.8A is higher than the maximum "Fast Rate" limit (3.75A).

- To get the absolute best of both worlds—the perfect 0.3C (2.25A) gentle charge current, Or 0.5C (3.75A) Fast Rate Current and the reliable 12.6V automatic safety cutoff—I would use a programmable (can be set) 10A Solar Charge Controller (either PWM or MPPT) that explicitly allows me to adjust the "Maximum Charging Current" parameter in its settings

Or

I would Calibrate an XL4016 Buck converter.

How to calibrate your XL4016 for your 4S pack:

Using an XL4016 Buck Converter as a charge controller is a popular DIY choice, but there is one critical requirement you must check on your specific module: it must have Current Limiting (CC) control.

There are two versions of the XL4016 board:

- Voltage Only: Has one adjustment screw (potentiometer). Do not use this; it will try to pull too many Amps from your panel and could overheat the battery.

- Voltage & Current (CC/CV): Has two (or three) adjustment screws. This is the one you need.

The XL4016 is a CC/CV (Constant Current / Constant Voltage) module, it has two adjustable screws, one for controlling current and one for controlling voltage.

To run the load while charging, I first set these limits using a DC adapter (19v, 3 Amps – 5 Amps) connected to my wall socket before I connect the battery.

- Set the Voltage (CV): Connect your 110W solar panel to the "IN" terminals. Turn the voltage screw until the "OUT" reads 12.6V exactly. This ensures the battery never overcharges.

- Set the Current (CC): This is the "speed limit" for charging.

  - Since your pack is 8Ah, a safe limit is 3A to 4A.

  - To set this, you usually need to short the output terminals through your multimeter (on the 10A setting) and turn the current screw until it reads your desired Amps.

- Add a Blocking Diode: Most XL4016 modules do not have backflow protection.

  - The Danger: At night, power will flow backwards from your battery into the XL4016, draining your battery and potentially burning out the chip.

  - The Fix: Solder a 10A Schottky Diode on the positive wire between the XL4016 "OUT+" and your Battery/BMS.

Using the Load Simultaneously

Since you want to run the motors while charging:

- Connect the XL4016 Output to your BMS (P+ and P-).

- Connect your Motor Buck Converters to the same BMS (P+ and P-).

- The Flow: When the sun is out, the XL4016 provides power. The motors will take what they need first, and any "leftover" current will flow into the battery. If the motors need more than the sun provides, the battery will instantly "help" by providing the difference.

One Major Warning

The XL4016 is a Buck Converter, not an MPPT controller.

- It only works if the Solar Panel Voltage (18V-21V) is higher than the Battery Voltage (16.8V).

- On a very cloudy day, if your panel voltage drops below 17V, the XL4016 will stop charging entirely.

7. BMS Sizing

To determine the ideal BMS for your 3S27P pack, we first need to translate your "Wh" load into "Amps," as BMS units are rated by current (Amps), not energy (Wh).

1. Calculating Your Current Draw

Since you are using a 3S (3 cells in series) Li-ion pack, your nominal voltage is 11.1V (3.7V per cell).

- Load Power: 69.8 W

- Formula: Amps (A) = Watts (W) / Volts (V)

- Calculation: 69.8W / 12V approx. 5.8A

Your device will pull approximately 5.8 Amps continuously.

2. The Ideal BMS Rating

To ensure the BMS doesn't overheat or "trip" during a minor surge, you should apply a 40% safety buffer.

i.e. 5.8 + (0.4 x 5.8) = 8.12

- Minimum Rating: 12A (too close for comfort)

- Ideal Rating: 15A to 20A

A 15A or 20A S BMS is the "sweet spot" for your setup. It is large enough to handle your 69.8W load with ease but small enough to remain cost-effective and compact.

Setting the current and voltage on XL4016 Buck converter

Perfect! Having two adjustment screws means your XL4016 is a CC/CV (Constant Current / Constant Voltage) module. This is exactly what you need to safely charge a Lithium-ion battery.

One screw controls the Voltage (your "pressure" limit), and the other controls the Amperage (your "speed" limit).

How to calibrate your XL4016 for your 4S pack:

To run your load while charging, you must set these limits before you connect the battery:

- Set Voltage (CV):

  - Connect your 19V DC wall adapter to the IN+ / IN- terminals for calibration.

  - With the output wires disconnected, I used the multimeter to measure the voltage at the OUT+ / OUT- terminals.

  - Ordinarily, I should turn the voltage potentiometer until the display reads 16.8V (which is 4S full-charge limit), but because I intend to connect a Schottky diode at the output terminal of the XL4016 (to prevent power going in reverse at night), the Schottky diode causes a 0.4V drop, so I turn the voltage potentiometer until the display reads 17.2V at the OUT terminals. This ensures exactly 16.8V reaches the battery after passing through the diode.

  - Note: If using the short-circuit method, ensure the current pot is turned mostly counter-clockwise before touching the probes to avoid a sudden high-current spark that could blow your multimeter's internal fuse.

- Set Current (CC):

  - Switch your multimeter to the 10A DC (or 20A DC) setting and move the red probe to the 10A (or 20A) port.

  - Touch the probes directly to the OUT+ and OUT- terminals (this creates a temporary short circuit).

  - Turn the current potentiometer until the meter reads 3.0A to 4.0A. This ensures the XL4016 won't pull too much current from the solar panel and won't charge your battery too fast.

The "Night Flow" Warning

Since you are using a Buck Converter instead of a dedicated Solar Charge Controller, you have a leakage problem:

- The Issue: At night, when the sun goes down, the XL4016 will remain "on" by pulling power backwards from your battery. This will slowly drain your 4S pack and could damage the XL4016 chip over time.

- The Solution: I installed a blocking diode (like a 10A Schottky diode) on the positive output wire of the XL4016 before it reaches the battery.

Final Wiring for "Simultaneous Use"

To make sure your motors can run while the sun is charging the battery:

- Solar Panel

XL4016 IN.

- XL4016 OUT (+ with Diode)

BMS (P+).

- XL4016 OUT (-)

BMS (P-).

- Your Load (Motor Buck Converters)

Also connect to BMS (P+ and P-).

The Logic: When the sun is high, the XL4016 provides the 4A you set. If your motors pull 3A, they take it directly from the XL4016, and the remaining 1A goes into the battery. If the motors pull 6A, they take all 4A from the sun and "borrow" the remaining 2A from the battery.

Diode to pick for blocking current from flowing:
10A Schottky diode 10SQ045 or 10SQ050

Type of Charge controller to use

The Lithium Charging Profile (CC/CV)

A Lithium-specific controller uses a Constant Current / Constant Voltage (CC/CV) algorithm:

- Stage 1 (CC): It sends a steady current (Amps) into the battery until the pack reaches 12.6V.

- Stage 2 (CV): Once it hits 12.6V, it holds that voltage steady while the current slowly drops to zero. This "tops off" the battery safely.

3. Recommended Controller Types

When shopping for your Hub, look for these specific models:

- 10A PWM Lithium Controller: These are very common and affordable. They usually have a "Blue" or "Black" casing with an LCD screen. You must enter the settings menu and select the battery type "b02" or "Li" (depending on the brand).

- MPPT 3S Li-ion Dedicated Module: These are often small green or blue circuit boards without a screen. They are pre-set specifically for 3S packs ($12.6V cut-off) and are highly efficient.

4. How to Spot a Lithium-Specific Controller

When looking at the specifications or the LCD screen, check for these three things:

- Adjustable Voltage: You can manually set the "Charge Limit" to 12.6V.

- No Equalization: The manual should state that "Equalization" is disabled for Lithium modes.

- Low Voltage Disconnect (LVD): It should allow you to set a "Cut-off" at around 9.0V to 10.0V to protect the cells from over-discharging.

Final Power Rail Setup (The Master Hub)

On your board, the flow should look like this:

- Solar Panel (30W)  Solar Charge Controller  BMS (P+/P-).

- BMS (B+/B1/B2/B-)  Lithium-ion Pack (3S4P).

- BMS (P+/P-)  Master Switch  Buck Converters.

Safety Tip for the Students: Always tell the judges: "We used a 20A BMS to ensure that even if a motor stalls, the BMS will cut power before the Lithium-ion cells can overheat, ensuring a fail-safe industrial design."